## Sheet1
Question |  | FMAA Answer | AECOM Answer
Where is the spoil material to be piled? |  | https://maps.app.goo.gl/ux2znbuHiHM5H3WB8 | #VALUE!
In regards to Q&A 41. If we detour traffic around the water/sewer tie-ins, we would like to divert traffic through the car wash site. |  | Using the site itself as a detour for initial tie-ins is an acceptable method provided the existing drainage ditch (temp culverts) and road edges are maintained and mud or gravel from the temporary road onto the rest of Snowbird Way and terminal parking lot area is accounted for with routine sweeping.
If the intent was to run the airport off water truck and pressure system, what was used it the past? Do you know the water volumes and the pressure required to run the airport? |  | The interuption to water would have to be carefully considered and planned for, with cooling systems included, we routinely exceed 1,250 litres per hour on a busy plus 25c summer day. There are periods in the spring months where the cooling tower, restaurants, and custodial/washroom water use is minimal e,g. Sunday and plus 10c weather. Water pressure in level 1 mech room reads ~85psi, supplying to the third floor of the building, we have a contingency plan for loss of water, we have not attempted to lose water and maintain the airport long term, but its possible. From the top floor to the basement there is some head pressure within the building, and sprinklers as fire protection would impacted as well. Things to plan for and communicate well during construction planning.
12. Does the 250mm gate valve on the storm line leaving the oil/water separator have any special gaskets or other attributes to be able to handle petroleum spills? Or is this a standard 250mm gate valve used in water systems. |  |  | Standard 250mm gate valve is required
Is this second gate valve circled in red required? |  |  | Yes.
3. Architectural Drawing A2 schedule W2 calls for 4" of Rigid insulation R30. The specification 07 21 00 div 2.1.4 calls for a Semi rigid Mineral wool RSI of 0.75 per 25.4mm (R 4.2 per 1 inch) thickness provides a total of R16.8. Would you clarify the corresponding type of insulation, thickness, and R value |  |  | Please see Addendum 1
1. Do the snow melt and in slab manifolds come complete with a control valve and ice/slab sensors for installation or will the controls contractor have to provide? |  |  | There is no control valve nor different zones for the snowmelt, they all run as one zone. The flow is controlled by the single circulator turning on and off. That circulator is in the snowmelt panel and is controlled by the snowmelt controller. The mixing valve for the snowmelt is built into the control panel c/w pump and controller. A snowmelt sensor can be provided to communicate with the controller and tell it when it senses snow/ice. The mixing valve ensures appropriate temperature to the manifolds. The single snow/ice detector and slab temperature sensor is located in the slab located outside of Washbay 12. Refer to schematic M-504 and View 3 on Plan Drawing M-104.
2. Will the Split Acs c/w a thermostat? Will they be BACnet capable or will they act as standalone and not be on the BAS? |  |  | The AC units will require an interface to communicate with the BMS / 3rd party thermostat. AC equipment manufacturer to provide an interface for BMS compatibility and controls contractor to provide thermostat / temperature transmitter.
3. Will the snow melt manifolds c/w a snow melt controller that is BACnet capable from the manufacturer or will the controls contractor be responsible for supplying a full controls solution? |  |  | The snowmelt controller in this panel is not bacnet compatible. This would need to be a different controller entirely. They are available however if that is what is preferred. Again, this isn't a per-manifold control system. They all run as one zone together (see Question 1 response). The optional bacnet snowmelt controller would be able to report what it is seeing but it won't know what each of the manifolds are doing/seeing as they are remote.
4. Will the In Floor heating manifolds c/w a controller that is BACnet capable from the manufacturer or will the controls contractor be responsible for supplying a full controls solution? |  |  | The controls contractor to provide a full controls solution to integrate the in-floor heating system with the BMS. Controls contractor to coordinate with the floor heating vendor after award.
Who is responsible to supply the gate and the Sliding Cantilever gate operator ? |  | Gate and Sliding Cantilever gate operator to be supplied and installed by awarded contractor.
There is no specification on the Poles for the exterior pole lights, can this please be provided |  | The intent was to match the terminal parking lot light poles. Data Plate can be sourced.
As per above question pole bases as shown on detail 2 drawing E000 show both power and communication conduits going in and out of each pole base, these conduits are 2” , I doubt there is enough space in each pole base to enter that amount of conduit, please confirm this is the intent. |  |  | 2" conduit is intended to allow for adequaite space to run multiple conductors/low voltage cables throughout the site from elec/comm room. Conduit can be transisted to a smaller size while entering pole base.
Referring to E100 regarding Pull boxes for Power and Communication, can a specification be provided for these boxes |  |  | Contractor to propose and submit pull box shop drawings for consultant to review.
Conduits depicted on E100 for underground all power and communications to be rigid PVC? |  |  | Yes
Do the conduits for the future fuel station need to comply with hazard location requirements from the building? If so, Will these require rated Pull boxes and Seals separate from the pull boxes shown for the site lighting and security? if so, can these conduits take a more direct route to limit the length and remove any underground pull boxes? |  |  | K. Peter Jarvenpaa, P.Eng., Principal Sea Island Projects Ltd. pjarvenpaa@seaislandprojects.ca 604.760.7524
Can the details for the Fuel Station be provided so we know what we are terminating to? |  |  | K. Peter Jarvenpaa, P.Eng., Principal Sea Island Projects Ltd. pjarvenpaa@seaislandprojects.ca 604.760.7524
Is the area within the car wash bays considered to be Category 1? |  |  | The area within the car wash bays is classified under Group F Division 2 Medium Hazard Industrial Occupancy. Please define what is meant by "Category 1"? (Low Hazard)
Referring to all equipment necessary in wash bays including disconnects and panels fire alarm pull stations, H/S and exit lights, as only a few items are rated as weatherproof, and given these areas will be subjected to direct streams of water should these be rated 4X rated? |  |  | Yes all inequiment subjected to direct streams of water s hall be rated 4X.
EMT is rated for wet areas as per CEC, are we permitted to use EMT with wet location fittings in the wash bay areas where not subjected to mechanical damage? |  |  | RMC shall be used in wash bay areas
Referring to the lighting control schedule- for exterior lighting, it is noted that the exterior lighting is to be dimmed accordingly to the daylight sensor- which lighting types does this note refer to, the wall mounted exterior lights, or the pole mounted exterior lights? |  |  | All building and parking exterior lights.
Specification 26 50 00 2.4 details differ from the luminaire schedule, which is correct? |  |  | Luminaire schedule on drawing E200 is correct. Luminaire schedule on Specification 26 50 00 2.4 shall be obseleted.
Noted on the drawings is an IT /Communications room, however there are no incoming conduits to the building are these missing? |  |  | Allow for 2 x 4" Rigid PVC stub up in the IT room. Telus is currently working on getting fibre service to this area and the demarcation point remain unknown.
Noted on drawings E100 are circuit requirements for the pole Lights , as per the security drawings there is a Security Cabinet at pole locations that will require 120-volt power, are these to be powered from the pole light circuit or are we to pull another circuit out to these? Can all the security cabinets share a circuit? |  |  | Security cabinet will require dedicated circuit to separate from lighting. Two 15A 120V circuits will be provided to north and south area. Addendum to follow to capture these changes.
Noted on security drawings are access controls for parking lot gates, no power is indicated on the drawing for any motorized gates, please confirm there is no requirements for power or conduits to the gates. |  |  | The "Existing Parking Lot Security and Communications Package" specifies that each gate will have a 2” rigid PVC conduit for power, which will terminate at MDP1. Additionally, each gate will require a 3C12AWG power cable from MDP1.
Please confirm security & comm QTA cable & conduit schedule as provided, conduits for gate systems seem excessively large. |  |  | 2" conduit shown on the electrical drawing is sufficient for communication cabling. Contractor shall provide junction box for fibre fusion splicing at each stop. 2" conduit shown on the electrical drawings is sufficient for automatic gate power. Addendum will follow to identify dedicated power circuit for the gate.
What does the Switching symbol in the wash bays depict? There is no symbol in the legend for this symbol. |  |  | Please provide an example of the "Switching symbol" refered to (Image and page number).
Workstation - is the airport supplying or are we responsible for supplying this hardware? It's not clear in the Spec. |  | Airport to install BMS and workstation as required.
1. Wall types W1, W2 and W5 call for 100mm rigid insulation (R30 min.). The spec calls for the below noted products, which will not give R30 in 4” of insulation. Please advise | #VALUE! | #VALUE! | Typo maybe, it should read as R20 for walls. This is achievable with 100 mm (4") of XPS, which provides about R5 per 25 mm (1"). Both products specified provide the noted thermal R-value.
2. There is no spec for the corrugated cladding. Which gauge do you require? |  |  | For corrugated cladding, recommended product is Vicwest 7/8" in 0.76 mm (22 ga.) base steel thickness
3. For division 07 42 16, would Proclad’s E-Panel be an acceptable alternate? See attached product information. |  |  | Proclad E-Panel is acceptable provided the product meets all performance and characteristics listed in Section 07 42 16, including but not limited to total panel thickness and fire performance (Fire-Resistant).
4. Some details show thermal clips, while others just show z-bar. No thermal clips are listed in the wall constructions. Are thermal clips required? |  |  | Yes, thermally improved cladding support system is required for this project.
Regarding RFP 25-003, we are asking if 1 single glaze Back Painted Spandrel would be a sufficient alternate to the Triple Glaze Spandrel noted (08 80 00). |  |  | No, preference is triple glaze to maintain the glazing performance throughout the façade. Gray frit on Surface #6?
1. Confirm the owner is providing and installing the fuel system? |  | Above ground fuel dispensing system components (tanks, hoses, meter, fire safety) will be supplied by the airport, the pad, conduit, and other design elements are to be supplied by the awarded contractor
2. Confirm the owner is providing and installing the carwash equipment? |  | The car wash wand, hose, pump, soap, suite and equipment system will be supplied by the airport, the wash bay and carwash equipment room and all other details within the design are to be supplied by the awarded contractor
3. Sec 07 52 16 Mod Bit Roof article 1.12.3 requires and ARCA warranty for the specified warranty period of 20 years. ARCA does not have a 20 (twenty) year warranty. 5 , 10 & 15 year warranties are available.Please advise which duration is preferred. |  |  | Provide 15 year warranty.
Could we have you provide a copy of the Geotechnical report. This will assist the civil, underground and insurance requirements. |  | Provided
Structural Drawing S322 sec J calls for 38 FRP grating. Do you have a specification?
2. Electrical Drawing E100 indicates a series of pull boxes. Can you provide a specification? |  |  | It is contractor's responsiblity to provide pull boxes product to meet code requirement as well as suiting site condition.
1. We have never seen a storm line daylight into a ditch. This storm line coming out of the stormceptor is 2.5M (8ft). What is protecting that pipe and more importantly that stormceptor from freezing. Cold air will travel in the outlet pipe and go into the stormceptor which does hold/retain water. It doesn’t fully drain like a manhole. |  | Storm system is typical for the airport fuel farm.
2. If the stormceptor does freeze who is responsible for the costly repair/replacement? |  | If installed to the design, owner will replace for items outside of stormceptor warranty.
3. From the pre-tender, there was mention that the airport would take the topsoil and dirt from the site grading. Please show the dump locations and the haul routes to get there. |  | Please utilize Snow Bird Way to Saline Cr Parkway to Snow Eagle Dr.
4. I assume the water connections will need to be done live, as we cannot turn the water service off to the airport. There is a valve on the mainline (circled in red). Are we to install this valve also? If so it will need to be an insertion valve to do it live. |  | 8pm to midnight has minimal airport demand. 3am to 6am also minimal demand for valve cutover. Possible to run airport off of water tank truck and pressure system. Ample notice will be required.
5. Can traffic be temporarily diverted around the traffic circle to open cut the water/sewer lines? The water line could be drilled with HDPE, but the sewer line is next to impossible to directional drill and hold a constant 0.5% unless you case bore in a steel casing. This would involve two subcontractors and a considerable extra cost. |  | Please share contractor's proposed plan with timing. There is potential for short timing temporary traffic diversion. For diversion, there would be a requirement to have either the North or South lane remaining open for fire access.
6. If we can divert the traffic, what is expected for a drive surface (cloth/grid, 300mm gravel?) and what would be expected for restoration (100mm topsoil/sod) or (150mm topsoil/seed)? |  | Traffic is expected to remain on the North or South lanes, and repave the first cut prior to opening the second set.
7. If we divert the traffic I assume we would be required to do full granular backfill in the excavations? |  | Yes
8. If we divert the traffic, we would need to restore all concrete and asphalt. What is the existing asphalt structure? We need to know what thickness to put back. |  | Asphalt structure is typical roadway standard for Ft McMurray.
9. I assume all landscape restoration for water/sewer is incidental to this work? |  | Landscape restoration is expected to be minimal
10. If we decide to go trenchless with the waterline, what size pipe would you like? 300MM HDPE DR 11? Or upsize the HDPE to account for extra pipe wall thickness in the HDPE. |  | Suggestion is open cut, if required for sanitary
11. If we go trenchless with the sanitary, would we be expected to do a case bore? If the expectation is to case bore, do you have a preferred casing pipe diameter/thickness/spec? Will we need cathodes, end caps or casing spacers? |  | Suggestion is open cut, if required for sanitary